## ALC-dSpace-mapping
ALC Controller
|  |  |  | Hardware | Hardware/Webctrl Settings
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  | Min/Max - Full Range | Min/Max - Half Range
DS6241 D/A - 16 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | Space Temp | AI | 0-5 V | Linear Full Range | 25/125F | 00:02 | AI-2 in VAV-8 |  | 25/125F | 25/225F
| 2 | 35/19 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  | 45/95F | 45/145F
| 3 | 3/36 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/10000CFM | 00:02 |  |  | 0/1400 | 0/2800
| 4 | 20/4 | VAV-2 East | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-7 |  | 25/125F | 25/225F
| 5 | 37/21 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  | 45/95F | 45/145F
| 6 | 22/6 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  |  | 0/1400 | 0/2800
| 7 | 39/23 | VAV-3 North | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-8 | 0 | 25/125F | 25/225F
| 8 | 7/40 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  | 45/95F | 45/145F
| 9 | 24/8 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  |  | 0/1400 | 0/2800
| 10 | 41/25 | VAV-4 South | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-9 |  | 25/125F | 25/225F
| 11 | 26/10 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  | 45/95F | 45/145F
| 12 | 43/27 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  |  | 0/1400 | 0/2800
| 13 | 11/44 | VAV-5 West | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-10 |  | 25/125F | 25/225F
| 14 | 28/12 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  | 45/95F | 45/145F
| 15 | 45/29 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  |  | 0/1400 | 0/2800
| 16 | 30/14 | OA | OF 1628-NR | OA Temp | AI | 0-10 V | Linear Full Range | -20/120F | 00:01 | (CHR-UI1) |  | -20/120F
| 17 | 47/31 |  |  | OA Humidity | AI | 0-10 V | Linear Full Range | 0/100 % | 00:02 | (CHR-UI2) | unlabeled | 0/100
| 18 | 15/48 | AHU |  | Duct static pressure | AI | 0-10 V | Linear w/ offset 2-12V | 0/0.2 psi | 00:04 | AHU-AI4
|  |  |  | Hardware | Hardware/Webctrl Settings
| Channel |  |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  | Min/Max
DS6221 A/D - 12 | 1 | 18/2 | VAV-6 (used as VAV-1) | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | CHR-UO1 (1628-NR)
| 2 | 35/19 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-6
| 3 | 3/36 | VAV-2 | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-7
| 4 | 20/4 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 5 | 37/21 | VAV-3 | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-8
| 6 | 22/6 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 7 | 39/23 | VAV-4 | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-9
| 8 | 7/40 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 9 | 24/8 | VAV-5 | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-10
| 10 | 41/25 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 18 | 1 | 18/2 | chiller plant |  | Head pressure control signal from CH | AI | 0-10V | Linear Full Range | ? | 00:04 | CHR-UI4
| 2 | 35/19 |  |  | CHW Supply Temperature | AI | 0-10V | Linear Full Range | 32/86F | 00:05 | CHR-UI5
| 3 | 3/36 |  |  | CW return temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:06 | CHR-UI6 | 20/45 C
| 4 | 20/4 |  |  | CHW return temperature | AI | 0-10V | Linear Full Range | 32/86F | 00:07 | CHR-UI7 | 8/24 C
| 5 | 37/21 |  |  | CW supply temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:08 | CHR-UI8
| 6 | 22/6 |  |  | CHWP status | BI | 0-10V |  | 0/1 | 00:09 | CHR-UI9
| 7 | 39/23 |  |  | CHW differential pressure | AI | 0-10V | Linear Full Range | 0/6 psi | 00:10 | CHR-UI10 | 18000/36000Pa
| 8 | 7/40 |  |  | CHW supply flow | AI | 0-10V | Linear Full Range | 0/10 lb/s | 00:11 | CHR-UI11 | 0/4 kg/s
| 9 | 24/8 |  |  | Loop CHW return temperature | AI | 0-10V | Linear Full Range | ? | 00:12 | CHR-UI12
| 10 | 41/25 |  |  | Plant CHW return temperature | AI | 0-10V | Linear Full Range | 32/86F | 00:13 | CHR-UI13
| 11 | 26/10 |  |  | CWP Status | BI | 0-10V |  | 0/1 | 00:14 | CHR-UI14
| 12 | 43/27 |  |  | CT status | BI | 0-10V |  | 0/1 | 00:15 | CHR-UI15
| 13 | 11/44 |  |  | Tower basin level | AI | 0-10V | Linear Full Range | ? | 00:16 | CHR-UI16
| 14 | 28/12 |  |  | WSE CW return temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:17 | CHR-UI17
| 15 | 45/29 |  |  | CHW return temperature before WSE | AI | 0-10V | Linear Full Range | 32/86F | 00:18 | CHR-UI18 | 20/45 C
| 16 | 30/14 |  |  | CHW return temperature after WSE | AI | 0-10V | Linear Full Range | 32/86F | 00:19 | CHR-UI19 | 10/30 C
| 17 | 47/31 |  |  | WSE CHW differential pressure | AI | 0-10V | Linear Full Range | 0/6 psi | 00:20 | CHR-UI20
| 18 | 15/48 | AHU |  | Supply air temperature | AI | 0-10V | Linear w/ offset 2-10V | 45/95F | 00:01 | AHU-AI1 | 53.24/64.4F
| 19 | 32/16 |  |  | Outdoor air flowrate | AI | 0-10V | Linear w/ offset 2-11V | 0/22000 CFM | 00:02 | AHU-AI2
| 20 | 49/33 |  |  | Mixed air temperature | AI | 0-10V | Linear w/ offset 2-12V | -20/120F | 00:03 | AHU-AI3
|  |  | AHU |  | SF Status | BI | 0-10V |  | 0/1
[5 empty] | Ret Fan Status | BI | 0-10V |  | 0/1
[5 empty] | RA Flow Sensor | AI | 0-10V |  | 0/22000 CFM
[5 empty] | Final Filter DP | AI | 0-10V
[5 empty] | RA Temp | AI | 0-10V |  | 25/125F
[5 empty] | SA Flow Sensor | AI | 0-10V |  | 0/22000 CFM
[5 empty] | Cooling Coil Ent Temp (air of water?) | AI | 0-10V |  | 32/95F
[5 empty] | Cooling Coil Lvg Temp | AI | 0-10V |  | 32/95F
[5 empty] | Heating Coil Ent Temp (air of water?) | AI | 0-10V |  | 32/95F
[5 empty] | Heating Coil Lvg Temp | AI | 0-10V |  | 32/95F
[5 empty] | Remote | BI
[5 empty] | Emergency Shutdown | BI
[5 empty] | Refrigerant Shutdown | BI
|  |  | Chiller Plant |  | CHWS Temp | AI
[5 empty] | CHWR Temp | AI
[5 empty] | CHW Flow | AI
[5 empty] | CH1 Head Pressure Control Signal | AI
[5 empty] | CH1 CHWS Temp | AI
[5 empty] | CH1 CWR Temp | AI
[5 empty] | CH1 CHWR Temp | AI
[5 empty] | CH1 CHW ISOV Status | BI
[5 empty] | CH1 CW ISOV Status | BI
[5 empty] | Local CHW Differential Pressure | AI
[5 empty] | CHWP1 Amps | AI
[5 empty] | CHWP1 Status | BI
|  |  | WSE CW |  | HX Diff Pressure | AI
[5 empty] | HX CWR Temp | AI
[5 empty] | CWP1 Status | BI
[5 empty] | CWS Temp | AI
[5 empty] | CWR Temp | AI
[5 empty] | CT1 Status | BI
[5 empty] | CHWRT before WSE | AI
[5 empty] | CHWRT After WSE | AI
[5 empty] | CT1 Basin Temp | AI
[5 empty] | Water Level | AI
Channel
DS6221 A/D - 14 | 1 | 18/2 | chiller plant |  | Chiller On/off | BO | 0-10V |  | 0/1 | 0:02 | CHR-UO2
| 2 | 35/19 |  |  | CHWST setpoint | AO | 0-10V | Linear Full Range | 41/50F | 1:02 | CHR-UO3
| 3 | 3/36 |  |  | CH CHW isolation valve | BO | 0-10V |  | 0/1 | 2:02 | CHR-UO4
| 4 | 20/4 |  |  | CH CHW bypass valve | BO | 0-10V |  | 0/1 | 3:02 | CHR-UO5
| 5 | 37/21 |  |  | CH CW isolation valve | BO | 0-10V |  | 0/1 | 4:02 | CHR-UO6
| 6 | 22/6 |  |  | CHWP start | BO | 0-10V |  | 0/1 | 5:02 | CHR-UO7
| 7 | 39/23 |  |  | CHWP speed | AO | 0-10V | Linear Full Range | 0/100 % | 6:02 | CHR-UO8
| 8 | 7/40 |  |  | CHW min flow bypass valve | AO | 0-10V | Linear Full Range | 0/100 % | 7:02 | CHR-UO9
| 9 | 24/8 |  |  | CWP start | BO | 0-10V |  | 0/1 | 8:02 | CHR-UO10
| 10 | 41/25 |  |  | CWP speed | AO | 0-10V | Linear Full Range | 0/100 % | 9:02 | CHR-UO11
| 11 | 26/10 |  |  | CT start | BO | 0-10V |  | 0/1 | 10:02 | CHR-UO12
| 12 | 43/27 |  |  | CT speed | AO | 0-10V | Linear Full Range | 0/100 % | 11:02 | CHR-UO13
| 13 | 11/44 |  |  | Makeup water level | BO | 0-10V |  | 0/1 | 12:02 | CHR-UO14
| 14 | 28/12 |  |  | WSE HX CW isolation valve | BO | 0-10V |  | 0/1 | 13:02 | CHR-UO15
| 15 | 45/29 |  |  | WSE CHW bypass valve | AO | 0-10V | Linear Full Range | 0/100 % | 14:02 | CHR-UO16
|  |  | AHU |  | SF S/S | BO | 0-10V |  | 0/1
[5 empty] | SF Spd% | AO | 0-10V |  | 0/100 %
[5 empty] | Cooling Valve | AO | 0-10V |  | 0/100 %
[5 empty] | Heating Valve | AO | 0-10V |  | 0/100 %
[5 empty] | Exhaust Damper | AO | 0-10V |  | 0/100 %
[5 empty] | Return Fan S/S | BO | 0-10V |  | 0/1
[5 empty] | Return Fan Speed | AO | 0-10V |  | 0/100 %
[5 empty] | Min. OA Damper | AO | 0-10V |  | 0/100 %
[5 empty] | RA Damper | AO | 0-10V |  | 0/100 %
[5 empty] | Economizer OA Damper | AO | 0-10V |  | 0/100 %
|  |  | Chiller |  | CH-1 Enable | BO
[5 empty] | CH-1 CHW Valve | AO
[5 empty] | CH-1 CW Isolation Valve | AO
[5 empty] | CHWP1 Enable | BO
[5 empty] | CHWP1 VFD Output | AO
[5 empty] | CHW Byp Valve | AO
[5 empty] | ECO CHW BYP VLV | BO
|  |  | WSE CW |  | HX CW Iso Valve Output | BO
[5 empty] | HX CHW Byp Vlv Output | AO
[5 empty] | CWP1 Enable | BO
[5 empty] | CWP-1 Speed | AO
[5 empty] | CT-1 Fan Enable | BO
[5 empty] | CT-1 VFD Speed | AO
[5 empty] | Makeup Valve | BO

## ALC-dSpace-mapping (2)
ALC Controller
|  |  |  | Hardware | Hardware/Webctrl Settings
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  |  | Min/Max - Full Range | Min/Max - Half Range
DS6241 D/A - 16 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | Space Temp | AI | 0-5 V | Linear Full Range | 25/125F | 00:02 | AI-2 in VAV-8 |  |  | 25/125F | 25/225F
| 2 | 35/19 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 3 | 3/36 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/10000CFM | 00:02 |  | 10000 | 487/9535 CFM | 0/1400 | 0/2800
| 4 | 20/4 | VAV-2 East | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-7 |  |  | 25/125F | 25/225F
| 5 | 37/21 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 6 | 22/6 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2000 | 105/1907 CFM | 0/1400 | 0/2800
| 7 | 39/23 | VAV-3 North | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-8 |  |  | 25/125F | 25/225F
| 8 | 7/40 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 9 | 24/8 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2100 | 105/2013 CFM | 0/1400 | 0/2800
| 10 | 41/25 | VAV-4 South | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-9 |  |  | 25/125F | 25/225F
| 11 | 26/10 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 12 | 43/27 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2100 | 105/2013 CFM | 0/1400 | 0/2800
| 13 | 11/44 | VAV-5 West | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-10 |  |  | 25/125F | 25/225F
| 14 | 28/12 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 15 | 45/29 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 1500 | 84/1484 CFM | 0/1400 | 0/2800
| 16 | 30/14 | [11 empty] | -20/120F
| 17 | 47/31 | [11 empty] | 0/100
| 18 | 15/48 | OA | OF 1628-NR | OA Temp | AI | 0-10 V | Linear Full Range | -20/120F | 00:01 | (CHR-UI1)
| 19 | 32/16 |  |  | OA Humidity | AI | 0-10 V | Linear Full Range | 0/100 % | 00:02 | (CHR-UI2)
| 20 | 49/33
|  |  |  | Hardware | Hardware/Webctrl Settings
| Channel |  |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  |  | Min/Max
DS6221 A/D - 12 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-6
| 2 | 35/19 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:02 | Not assigned
| 3 | 3/36 | VAV-2 East | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-7
| 4 | 20/4 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 5 | 37/21 | VAV-3 North | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-8
| 6 | 22/6 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 7 | 39/23 | VAV-4 South | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-9
| 8 | 7/40 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 9 | 24/8 | VAV-5 West | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-10
| 10 | 41/25 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 11 | 26/10 | AHU |  | SF S/S | BO | V ? | Relay / Triac Output | 0/1 ? | 00:01 | AHU-AO1
| 12 | 43/27 |  |  | SF Spd% | AO | 0-10V | Linear Full Range | 0/100 % | 00:02 | AHU-AO2
| 13 | 11/44 |  |  | RA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:03 | AHU-AO3
| 14 | 28/12 |  |  | Economizer OA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:04 | AHU-AO4
| 15 | 45/29 |  |  | Exhaust Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:05 | AHU-AO5
| 16 | 30/14 |  |  | Cooling Valve | AO | 0-10V | Linear Full Range | 0/100 % | 00:06 | AHU-AO6
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 18 | 1 | 18/2 | chiller |  | CHWS Temp | AI | 0-10V |  | 32/95F | 00:04 | CHR-UI4
| 2 | 35/19 |  |  | CHWR Temp | AI | 0-10V |  | 32/95F | 00:05 | CHR-UI5
| 3 | 3/36 |  |  | CHW Flow | AI | 0-10V |  | 0/10 lb/s | 00:06 | CHR-UI6
| 4 | 20/4 |  |  | CH1 Head Pressure Control Signal | AI | 0-10V |  |  | 00:07 | CHR-UI7
| 5 | 37/21 |  |  | CH1 CHW ISOV Status | BI | 0-10V |  | 0/1 | 00:08 | CHR-UI8
| 6 | 22/6 |  |  | CH1 CW ISOV Status | BI | 0-10V |  | 0/1 | 00:09 | CHR-UI9
| 7 | 39/23 |  |  | Local CHW Differential Pressure | AI | 0-10V |  | 0/6 psi | 00:10 | CHR-UI10
| 8 | 7/40 |  |  | CHWP1 Amps | AI | 0-10V |  |  | 00:11 | CHR-UI11
| 9 | 24/8 |  |  | CHWP1 Status | BI | 0-10V |  | 0/1 | 00:12 | CHR-UI12
| 10 | 41/25 | WSE CW |  | HX Diff Pressure | AI | 0-10V |  |  | 00:13 | CHR-UI13
| 11 | 26/10 |  |  | HX CWR Temp | AI | 0-10V |  |  | 00:14 | CHR-UI14
| 12 | 43/27 |  |  | CWP1 Status | BI | 0-10V |  | 0/1 | 00:15 | CHR-UI15
| 13 | 11/44 |  |  | CWS Temp | AI | 0-10V |  |  | 00:16 | CHR-UI16
| 14 | 28/12 |  |  | CWR Temp | AI | 0-10V |  |  | 00:17 | CHR-UI17
| 15 | 45/29 |  |  | CT1 Status | BI | 0-10V |  | 0/1 | 00:18 | CHR-UI18
| 16 | 30/14 |  |  | CHWRT before WSE | AI | 0-10V |  |  | 00:19 | CHR-UI19
| 17 | 47/31 |  |  | CHWRT After WSE | AI | 0-10V |  |  | 00:20 | CHR-UI20
| 18 | 15/48
| 19 | 32/16
| 20 | 49/33
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  | Pin(ref/sig)
DS6101 D/A - 10 | 3_1 | 26/10 | AHU |  | Supply air temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:01 | AHU-AI1 | 6_1 | 37/21
| 3_2 | 43/27 |  |  | Outdoor air flowrate | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:02 | AHU-AI2 | 6_2 | 22/6
| 3_3 | 11/44 |  |  | Mixed air temperature | AI | 0-10V | Linear Full Range | -20/120F | 00:03 | AHU-AI3 | 6_3 | 39/23
| 3_4 | 28/12 |  |  | Duct static pressure | AI | 0-10 V | Linear Full Range | 0/0.2 psi | 00:04 | AHU-AI4 | 6_4 | 7./40
| 3_5 | 45/29 |  |  | SF Status | BI | 0-5 V | Binary Input | 0/1 | 00:05 | AHU-AI5 | 6_5 | 24/8
| 3_6 | 30/14 |  |  | Ret Fan Status | BI | 0-5 V | Binary Input | 0/1 | 00:06 | AHU-AI6 | 6_6 | 41/25
| 3_7 | 47/31 |  |  | RA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:07 | AHU-AI7 | 6_7 | 26/10
| 3_8 | 15/48 |  |  | RA Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:08 | AHU-AI8 | 6_8 | 43/27
| 3_9 | 32/16 |  |  | SA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:09 | AHU-AI9 | 9_1 | 18/2
| 3_10 | 49/33 |  |  | Cooling Coil Ent Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:10 | AHU-AI10 | 9_2 | 35/19
| 4_1 | 18/2 |  |  | Cooling Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:11 | AHU-AI11 | 9_3 | 3./36
| 4_2 | 35/19 |  |  | Heating Coil Ent Temp | AI | 0-10V | Linear Full Range | -20/120F | 00:12 | AHU-AI12 | 9_4 | 20/4
| 4_3 | 3/36 |  |  | Heating Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:13 | AHU-AI13 | 7_1 | 15/48
| 4_4 | 20/4 | WSE CW |  | CT1 Basin Temp | AI
| 4_5 | 37/21 |  |  | Water Level | AI
| 4_6 | 22/6 | chiller |  | Remote | BI
| 4_7 | 39/23 |  |  | Emergency Shutdown | BI
| 4_8 | 7/40 |  |  | Refrigerant Shutdown | BI
| 4_9 | 24/8
| 4_10 | 41/25
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6221 A/D - 14 | 1 | 18/2 | chiller plant |  | CH-1 Enable | BO | 0-10V |  |  |  | CHR-UO2
| 2 | 35/19 |  |  | CH-1 CHW Valve | AO | 0-10V |  |  |  | CHR-UO3
| 3 | 3/36 |  |  | CH-1 CW Isolation Valve | AO | 0-10V |  |  |  | CHR-UO4
| 4 | 20/4 |  |  | CHWP1 Enable | BO | 0-10V |  |  |  | CHR-UO5
| 5 | 37/21 |  |  | CHWP1 VFD Output | AO | 0-10V |  |  |  | CHR-UO6
| 6 | 22/6 |  |  | CHW Byp Valve | AO | 0-10V |  |  |  | CHR-UO7
| 7 | 39/23 |  |  | ECO CHW BYP VLV | BO | 0-10V |  |  |  | CHR-UO8
| 8 | 7/40 | WSE CW |  | HX CW Iso Valve Output | BO | 0-10V |  |  |  | CHR-UO9
| 9 | 24/8 |  |  | HX CHW Byp Vlv Output | AO | 0-10V |  |  |  | CHR-UO10
| 10 | 41/25 |  |  | CWP1 Enable | BO | 0-10V |  |  |  | CHR-UO11
| 11 | 26/10 |  |  | CWP-1 Speed | AO | 0-10V |  |  |  | CHR-UO12
| 12 | 43/27 |  |  | CT-1 Fan Enable | BO | 0-10V |  |  |  | CHR-UO13
| 13 | 11/44 |  |  | CT-1 VFD Speed | AO | 0-10V |  |  |  | CHR-UO14
| 14 | 28/12 |  |  | Makeup Valve | BO | 0-10V |  |  |  | CHR-UO15
| 15 | 45/29
| 16 | 30/14 | AHU |  | Heating Valve | AO | 0-10V | Linear Full Range | 0/100 % |  | AHU-AO7
|  |  | AHU |  | Return Fan S/S | BO | 0-10V | Relay / Triac Output | 0/1
[5 empty] | Return Fan Speed | AO | 0-10V | Linear Full Range | 0/100 %

## ALC-dSpace-mapping (3)
ALC Controller
|  |  |  | Hardware | Hardware/Webctrl Settings
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  |  | Min/Max - Full Range | Min/Max - Half Range
DS6241 D/A - 16 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | Space Temp | AI | 0-5 V | Linear Full Range | 25/125F | 00:02 | AI-2 in VAV-8 |  |  | 25/125F | 25/225F
| 2 | 35/19 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 3 | 3/36 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/10000CFM | 00:02 |  | 10000 | 487/9535 CFM | 0/1400 | 0/2800
| 4 | 20/4 | VAV-7 (used as VAV-2) East | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | (00:01) 00:03 | (AI-1 in VAV-7) CHR-UI3 |  |  | 25/125F | 25/225F
| 5 | 37/21 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 6 | 22/6 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2000 | 105/1907 CFM | 0/1400 | 0/2800
| 7 | 39/23 | VAV-3 North | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-8 |  |  | 25/125F | 25/225F
| 8 | 7/40 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 9 | 24/8 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2100 | 105/2013 CFM | 0/1400 | 0/2800
| 10 | 41/25 | VAV-4 South | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-9 |  |  | 25/125F | 25/225F
| 11 | 26/10 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 12 | 43/27 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 2100 | 105/2013 CFM | 0/1400 | 0/2800
| 13 | 11/44 | VAV-5 West | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-10 |  |  | 25/125F | 25/225F
| 14 | 28/12 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01 |  |  |  | 45/95F | 45/145F
| 15 | 45/29 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02 |  | 1500 | 84/1484 CFM | 0/1400 | 0/2800
| 16 | 30/14 | [11 empty] | -20/120F
| 17 | 47/31 | [11 empty] | 0/100
| 18 | 15/48 | OA | OF 1628-NR | OA Temp | AI | 0-10 V | Linear Full Range | -20/120F | 00:01 | (CHR-UI1)
| 19 | 32/16 |  |  | OA Humidity | AI | 0-10 V | Linear Full Range | 0/100 % | 00:02 | (CHR-UI2)
| 20 | 49/33
|  |  |  | Hardware | Hardware/Webctrl Settings
| Channel |  |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  |  | Min/Max
DS6221 A/D - 12 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-6
| 2 | 35/19 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % |  | Not assigned
| 3 | 3/36 | VAV-2 East | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-7
| 4 | 20/4 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % |  | Not assigned
| 5 | 37/21 | VAV-3 North | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-8
| 6 | 22/6 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 7 | 39/23 | VAV-4 South | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-9
| 8 | 7/40 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 9 | 24/8 | VAV-5 West | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-10
| 10 | 41/25 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 11 | 26/10 | AHU |  | SF S/S | BO | V ? | Relay / Triac Output | 0/1 ? | 00:01 | AHU-AO1
| 12 | 43/27 |  |  | SF Spd% | AO | 0-10V | Linear Full Range | 0/100 % | 00:02 | AHU-AO2
| 13 | 11/44 |  |  | RA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:03 | AHU-AO3
| 14 | 28/12 |  |  | Economizer OA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:04 | AHU-AO4
| 15 | 45/29 |  |  | Exhaust Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:05 | AHU-AO5
| 16 | 30/14 |  |  | Cooling Valve | AO | 0-10V | Linear Full Range | 0/100 % | 00:06 | AHU-AO6
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 18 | 1 | 18/2 | AHU |  | Supply air temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:01 | AHU-AI1
| 2 | 35/19 |  |  | Outdoor air flowrate | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:02 | AHU-AI2
| 3 | 3/36 |  |  | Mixed air temperature | AI | 0-10V | Linear Full Range | -20/120F | 00:03 | AHU-AI3
| 4 | 20/4 |  |  | Duct static pressure | AI | 0-10 V | Linear Full Range | 0/0.2 psi | 00:04 | AHU-AI4
| 5 | 37/21 |  |  | SF Status | BI | 0-10 V | Binary Input | 0/1 | 00:05 | AHU-AI5
| 6 | 22/6 |  |  | Ret Fan Status | BI | 0-10 V | Binary Input | 0/1 | 00:06 | AHU-AI6
| 7 | 39/23 |  |  | RA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:07 | AHU-AI7
| 8 | 7/40 |  |  | RA Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:08 | AHU-AI8
| 9 | 24/8 |  |  | SA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:09 | AHU-AI9
| 10 | 41/25 |  |  | Cooling Coil Ent Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:10 | AHU-AI10
| 11 | 26/10 |  |  | Cooling Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:11 | AHU-AI11
| 12 | 43/27 |  |  | Heating Coil Ent Temp | AI | 0-10V | Linear Full Range | -20/120F | 00:12 | AHU-AI12
| 13 | 11/44 |  |  | Heating Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:13 | AHU-AI13
| 14 | 28/12 | WSE CW |  | CT1 Basin Temp | AI
| 15 | 45/29 |  |  | Water Level | AI
| 16 | 30/14 | chiller |  | Remote | BI
| 17 | 47/31 |  |  | Emergency Shutdown | BI
| 18 | 15/48 |  |  | Refrigerant Shutdown | BI
| 19 | 32/16
| 20 | 49/33
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num |  |  | Pin(ref/sig)
DS6101 D/A - 10 | 3_1 | 26/10 | AHU |  | Supply air temperature | AI | 0-10V | Linear Full Range | 25/125F | 00:01 | AHU-AI1 | 6_1 | 37/21
| 3_2 | 43/27 |  |  | Outdoor air flowrate | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:02 | AHU-AI2 | 6_2 | 22/6
| 3_3 | 11/44 |  |  | Mixed air temperature | AI | 0-10V | Linear Full Range | -20/120F | 00:03 | AHU-AI3 | 6_3 | 39/23
| 3_4 | 28/12 |  |  | Duct static pressure | AI | 0-10 V | Linear Full Range | 0/0.2 psi | 00:04 | AHU-AI4 | 6_4 | 7./40
| 3_5 | 45/29 |  |  | SF Status | BI | 0-10 V | Binary Input | 0/1 | 00:05 | AHU-AI5 | 6_5 | 24/8
| 3_6 | 30/14 |  |  | Ret Fan Status | BI | 0-10 V | Binary Input | 0/1 | 00:06 | AHU-AI6 | 6_6 | 41/25
| 3_7 | 47/31 |  |  | RA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:07 | AHU-AI7 | 6_7 | 26/10
| 3_8 | 15/48 |  |  | RA Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:08 | AHU-AI8 | 6_8 | 43/27
| 3_9 | 32/16 |  |  | SA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 00:09 | AHU-AI9 | 9_1 | 18/2
| 3_10 | 49/33 |  |  | Cooling Coil Ent Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:10 | AHU-AI10 | 9_2 | 35/19
| 4_1 | 18/2 |  |  | Cooling Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:11 | AHU-AI11 | 9_3 | 3./36
| 4_2 | 35/19 |  |  | Heating Coil Ent Temp | AI | 0-10V | Linear Full Range | -20/120F | 00:12 | AHU-AI12 | 9_4 | 20/4
| 4_3 | 3/36 |  |  | Heating Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 00:13 | AHU-AI13 | 7_1 | 15/48
| 4_4 | 20/4 | WSE CW |  | CT1 Basin Temp | AI
| 4_5 | 37/21 |  |  | Water Level | AI
| 4_6 | 22/6 | chiller |  | Remote | BI
| 4_7 | 39/23 |  |  | Emergency Shutdown | BI
| 4_8 | 7/40 |  |  | Refrigerant Shutdown | BI
| 4_9 | 24/8
| 4_10 | 41/25
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6221 A/D - 14 | 1 | 18/2 | chiller plant |  | CH-1 Enable | BO | 0-10V |  |  |  | CHR-UO2
| 2 | 35/19 |  |  | CH-1 CHW Valve | AO | 0-10V |  |  |  | CHR-UO3
| 3 | 3/36 |  |  | CH-1 CW Isolation Valve | AO | 0-10V |  |  |  | CHR-UO4
| 4 | 20/4 |  |  | CHWP1 Enable | BO | 0-10V |  |  |  | CHR-UO5
| 5 | 37/21 |  |  | CHWP1 VFD Output | AO | 0-10V |  |  |  | CHR-UO6
| 6 | 22/6 |  |  | CHW Byp Valve | AO | 0-10V |  |  |  | CHR-UO7
| 7 | 39/23 |  |  | ECO CHW BYP VLV | BO | 0-10V |  |  |  | CHR-UO8
| 8 | 7/40 | WSE CW |  | HX CW Iso Valve Output | BO | 0-10V |  |  |  | CHR-UO9
| 9 | 24/8 |  |  | HX CHW Byp Vlv Output | AO | 0-10V |  |  |  | CHR-UO10
| 10 | 41/25 |  |  | CWP1 Enable | BO | 0-10V |  |  |  | CHR-UO11
| 11 | 26/10 |  |  | CWP-1 Speed | AO | 0-10V |  |  |  | CHR-UO12
| 12 | 43/27 |  |  | CT-1 Fan Enable | BO | 0-10V |  |  |  | CHR-UO13
| 13 | 11/44 |  |  | CT-1 VFD Speed | AO | 0-10V |  |  |  | CHR-UO14
| 14 | 28/12 |  |  | Makeup Valve | BO | 0-10V |  |  |  | CHR-UO15
| 15 | 45/29 |  |  | Min. OA Damper | AO | 0-10V | Linear Full Range | 0/100 % |  | AHU-AO8
| 16 | 30/14 | AHU |  | Heating Valve | AO | 0-10V | Linear Full Range | 0/100 % |  | AHU-AO7
|  |  | AHU |  | Return Fan S/S | BO | 0-10V | Relay / Triac Output | 0/1
[5 empty] | Return Fan Speed | AO | 0-10V | Linear Full Range | 0/100 %

## ALC-dSpace-mapping (4)
ALC Controller
|  |  |  | Hardware | Hardware/Webctrl Settings
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 16 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | Space Temp | AI | 0-5 V | Linear Full Range | 25/125F | 00:02 | AI-2 in VAV-8
| 2 | 35/19 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 3 | 3/36 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/10000CFM | 00:02
| 4 | 20/4 | VAV-7 (used as VAV-2) East | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:03 | CHR-UI3
| 5 | 37/21 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 6 | 22/6 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02
| 7 | 39/23 | VAV-3 North | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-8
| 8 | 7/40 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 9 | 24/8 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02
| 10 | 41/25 | VAV-4 South | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-9
| 11 | 26/10 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 12 | 43/27 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02
| 13 | 11/44 | VAV-5 West | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | AI-1 in VAV-10
| 14 | 28/12 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 15 | 45/29 |  |  | Flow Input | AI | 0-5V | Linear Full Range | 0/3000CFM | 00:02
| 16 | 30/14
| 17 | 47/31
| 18 | 15/48 | OA | OF 1628-NR | OA Temp | AI | 0-10 V | Linear Full Range | -20/120F | 00:01 | (CHR-UI1)
| 19 | 32/16 |  |  | OA Humidity | AI | 0-10 V | Linear Full Range | 0/100 % | 00:02 | (CHR-UI2)
| 20 | 49/33
|  |  |  | Hardware | Hardware/Webctrl Settings
| Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6221 A/D - 12 | 1 | 18/2 | VAV-6 (used as VAV-1) Core | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-6
| 2 | 35/19 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % |  | Not assigned
| 3 | 3/36 | VAV-7 (used as VAV-2) East | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-7
| 4 | 20/4 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % |  | Not assigned
| 5 | 37/21 | VAV-3 North | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-8
| 6 | 22/6 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 7 | 39/23 | VAV-4 South | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-9
| 8 | 7/40 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 9 | 24/8 | VAV-5 West | ZN431A | External Air Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:01 | AO-1 in VAV-10
| 10 | 41/25 |  |  | Heat AO | AO | 0-10V | Linear Full Range | 0/100 % | 00:01
| 11 | 26/10 | AHU |  | SF S/S | BO | 0/9 V | Relay / Triac Output | 0/1 | 00:01 | AHU-AO1
| 12 | 43/27 |  |  | SF Spd% | AO | 0-10V | Linear Full Range | 0/100 % | 00:02 | AHU-AO2
| 13 | 11/44 |  |  | RA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:03 | AHU-AO3
| 14 | 28/12 |  |  | Economizer OA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:04 | AHU-AO4
| 15 | 45/29 |  |  | Exhaust Damper | AO | 0-10V | Linear Full Range | 0/100 % | 00:05 | AHU-AO5
| 16 | 30/14 |  |  | Cooling Valve | AO | 0-10V | Linear Full Range | 0/100 % | 00:06 | AHU-AO6
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 18 | 1 | 18/2 | AHU |  | Supply air temperature | AI | 0-10V | Linear Full Range | 25/125F | 01:01 | AHU-AI1
| 2 | 35/19 |  |  | Outdoor air flowrate | AI | 0-10V | Linear Full Range | 0/22000 CFM | 01:02 | AHU-AI2
| 3 | 3/36 |  |  | Mixed air temperature | AI | 0-10V | Linear Full Range | -20/120F | 01:03 | AHU-AI3
| 4 | 20/4 |  |  | Duct static pressure | AI | 0-10 V | Linear Full Range | 0/0.2 psi | 01:04 | AHU-AI4
| 5 | 37/21 |  |  | SF Status | BI | 0/10 V | Binary Input | 0/1 | 01:05 | AHU-AI5
| 6 | 22/6 |  |  | Ret Fan Status | BI | 0/10 V | Binary Input | 0/1 | 01:06 | AHU-AI6
| 7 | 39/23 |  |  | RA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 01:07 | AHU-AI7
| 8 | 7/40 |  |  | RA Temp | AI | 0-10V | Linear Full Range | 25/125F | 01:08 | AHU-AI8
| 9 | 24/8 |  |  | SA Flow Sensor | AI | 0-10V | Linear Full Range | 0/22000 CFM | 01:09 | AHU-AI9
| 10 | 41/25 |  |  | Cooling Coil Ent Temp | AI | 0-10V | Linear Full Range | 25/125F | 01:10 | AHU-AI10
| 11 | 26/10 |  |  | Cooling Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 01:11 | AHU-AI11
| 12 | 43/27 |  |  | Heating Coil Ent Temp | AI | 0-10V | Linear Full Range | -20/120F | 01:12 | AHU-AI12
| 13 | 11/44 |  |  | Heating Coil Lvg Temp | AI | 0-10V | Linear Full Range | 25/125F | 02:01 | AHU-AI13
| 14 | 28/12 | Chiller Plant |  | CH1 HPC Sig | AI | 0-10V | Linear Full Range | 0/100 % | 00:16 | CHR-UI16
| 15 | 45/29 |  |  | CHW Flow | AI | 0-10V | Linear Full Range | 0/80 gpm | 00:17 | CHR-UI17
| 16 | 30/14 |  |  | CHWR Temp / CH1 CHWR Temp | AI | 0-10V | Linear Full Range | 39/68 F | 00:18 | CHR-UI18
| 17 | 47/31 |  |  | CHWS Temp / CH1 CHWS Temp | AI | 0-10V | Linear Full Range | 39/68 F | 00:19 | CHR-UI19
| 18 | 15/48 |  |  | Local CHW DP | AI | 0-10V | Linear Full Range | 0/5.2213586 psi | 00:20 | CHR-UI20
| 19 | 32/16 |  |  | CHWP2 Amps (used as Cooling Mode Control Signal) | AI | 0-5V | Linear Full Range | 0/5 | 00:21 | CHR-UI21
| 20 | 49/33
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6101 D/A - P1 | DO 3 Ch. 1 | 1 / 18 | Chiller Plant |  | CH1 CHW ISOV Status | BI | 0/10V | Binary Input | 0/1 | 00:04 | CHR-UI4
| DO 3 Ch. 2 | 5 / 2 |  |  | CH1 CW ISOV Status | BI | 0/10V | Binary Input | 0/1 | 00:05 | CHR-UI5
| DO 3 Ch. 3 | 9 / 35 |  |  | CHWP1 Status | BI | 0/10V | Binary Input | 0/1 | 00:06 | CHR-UI6
| DO 3 Ch. 4 | 13 / 19 | WSE CW |  | CT1 Status | BI | 0/10V | Binary Input | 0/1 | 00:07 | CHR-UI7
| DO 3 Ch. 5 | 17 / 20 |  |  | CWP1 Status | BI | 0/10V | Binary Input | 0/1 | 00:08 | CHR-UI8
DS6101 D/A - P3 | AO 6 Ch. 1 | 37 / 21 |  |  | CHWRT After WSE | AI | 0-10V | Linear Full Range | 39/68 F | 00:09 | CHR-UI9
| AO 6 Ch. 2 | 22 / 6 |  |  | CHWRT before WSE | AI | 0-10V | Linear Full Range | 39/68 F | 00:18 | CHR-UI10
| AO 6 Ch. 3 | 39 / 23 |  |  | CT1 Basin Temp | AI | 0-10V | Linear Full Range | 59/113 F | 00:11 | CHR-UI11
| AO 6 Ch. 4 | 7 / 40 |  |  | HX Diff Pressure | AI | 0-10V | Linear Full Range | 0/5.2213586 psi | 00:12 | CHR-UI12
| AO 6 Ch. 5 | 24 / 8 |  |  | CWS Temp | AI | 0-10V | Linear Full Range | 59/113 F | 00:13 | CHR-UI13
| AO 6 Ch. 6 | 41 / 25 |  |  | CWR Temp / CH1 CWR Temp | AI | 0-10V | Linear Full Range | 59/113 F | 00:14 | CHR-UI14
| AO 6 Ch. 7 | 26 / 10 |  |  | HX CWR Temp | AI | 0-10V | Linear Full Range | 59/113 F | 00:15 | CHR-UI15
DS6101 D/A - P3 | AO 6 Ch. 8 | 43/27 | Power Consumption |  | total power | AI | 0-5V | Linear Full Range | 0/50000 W | 00:01 | AI-1 in VAV-1
| AO 9 Ch. 1 | 18/2 |  |  | chiller power | AI | 0-5V | Linear Full Range | 0/30000 W | 00:02 | AI-2 in VAV-1
| AO 9 Ch. 2 | 35/19 |  |  | fan power | AI | 0-5V | Linear Full Range | 0/10000 W | 00:01 | AI-1 in VAV-2
| AO 9 Ch. 3 | 3/36 |  |  | chw pump power | AI | 0-5V | Linear Full Range | 0/5000 W | 00:02 | AI-2 in VAV-2
| AO 9 Ch. 4 | 20/4 |  |  | CT power | AI | 0-5V | Linear Full Range | 0/8000 W | 00:02 | AI-2 in VAV-10
Board-Slot | Channel | Pin(ref/sig) |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6221 A/D - 14 | 1 | 18/2 | Chiller Plant |  | CH-1 Enable | BO | 0-10V | Binary Output | 0/1 | 00:01 | CHR-UO1
| 2 | 35/19 |  |  | CH-1 CHW Valve | AO | 0-10V | Linear Full Range | 0/100 % | 00:02 | CHR-UO2
| 3 | 3/36 |  |  | CHWP1 Enable | BO | 0-10V | Binary Output | 0/1 | 00:03 | CHR-UO3
| 4 | 20/4 |  |  | CHWP1 VFD Output | AO | 0-10V | Linear Full Range | 0/100 % | 00:04 | CHR-UO4
| 5 | 37/21 |  |  | ECO CHW BYP VLV | BO | 0-10V | Binary Output | 0/1 | 00:05 | CHR-UO5
| 6 | 22/6 |  |  | CH-1 CW Isolation Valve | AO | 0-10V | Linear Full Range |  | 00:06 | CHR-UO6
| 7 | 39/23 |  |  | CHW Byp Valve | AO | 0-10V | Linear Full Range |  | 00:07 | CHR-UO7
| 8 | 7/40 | WSE CW |  | CWP1 Enable | BO | 0-10V | Binary Output | 0/1 | 00:08 | CHR-UO8
| 9 | 24/8 |  |  | CWP-1 Speed | AO | 0-10V | Linear Full Range | 0/100 % | 00:09 | CHR-UO9
| 10 | 41/25 |  |  | CT-1 Fan Enable | BO | 0-10V | Binary Output | 0/1 | 00:10 | CHR-UO10
| 11 | 26/10 |  |  | CT-1 VFD Speed | AO | 0-10V | Linear Full Range | 0/100 % | 00:11 | CHR-UO11
| 12 | 43/27 |  |  | HX CHW Byp Vlv Output | AO | 0-10V | Linear Full Range | 0/100 % | 00:12 | CHR-UO12
| 13 | 11/44 |  |  | HX CW Iso Valve Output | BO | 0-10V | Binary Output |  | 00:13 | CHR-UO13
| 14 | 28/12 |  |  | Makeup Valve | BO | 0-10V | Binary Output |  | 00:14 | CHR-UO14
| 15 | 45/29 |  |  | Min. OA Damper | AO | 0-10V | Linear Full Range | 0/100 % | 01:08 | AHU-AO8
| 16 | 30/14 | AHU |  | Heating Valve | AO | 0-10V | Linear Full Range | 0/100 % | 01:07 | AHU-AO7